## Land Use
DEVELOPMENT LAND USE INPUT
Input | Calculated |  |  | Input | Given | Calculated | Calculated | Given | Calculated | Given | Given
Area Zoned | Percent Zone | Zone |  | Density | Equivalent | Equivalent | Equivalent | Capita Usage | Average WWP | Infiltration | Inflow Coeff
acres | as decimal | Type | Land Use Description | units/acre | capita/unit | capita/acre | Capita | gal/capita/day | gal/acre/day | gal/acre/day | K
0 | 0 | 1 | Very Low Density Res | 1 | 2.3 | 2.3 | 0 | 100 | 230 | 500 | 0.0035
0 | 0 | 2 | Low Density Res | 4 | 2.3 | 9.2 | 0 | 100 | 920 | 500 | 0.0035
0 | 0 | 3 | Medium Density Res | 12 | 2.3 | 27.6 | 0 | 100 | 2760 | 500 | 0.0035
0 | 0 | 4 | Office//Multi Family | 12 | 2.3 | 27.6 | 0 | 100 | 2760 | 200 | 0.003
1.08 | 1 | 5 | Office/Commercial | 2 | 3 | 6 | 6.48 | 100 | 600 | 200 | 0.003
0 | 0 | 6 | Heavy Industry | 1 | 25 | 25 | 0 | 100 | 2500 | 200 | 0.003
0 | 0 | 7 | Public | 1 | 7 | 7 | 0 | 100 | 700 | 0 | 0.0005
0 | 0 | 8 | Agriculture/Park | 1 | 1 | 1 | 0 | 100 | 100 | 0 | 0.0005
1.08 | 1 |  | Calculated Weighted Averages | 2 | 3 | 6 | 6.48 | 100 | 600 | 200 | 0.003

## Design Flow
DEVELOPMENT DESIGN FLOW CALCULATION
Inflow +
Peak WWP +
[8 empty] | Infiltration = |  |  | Calculated
[5 empty] | Calculated | Calculated | Calculated | Calculated | Calculated | Calculated | Design Flow/ADF | Calculated | Calculated
| Developed | Tc | 10 Yr i | WWP | Inflow | Peak WWP | Infiltration | Design Flow | Design Flow | ADF | Peaking | Equivalent | Design Flow
| (acres) | (minutes) | (in/hr) | Peaking Factor | (cfs) | (cfs) | (cfs) | (cfs) | (mgd) | (mgd) | Factor | Population | (gpm)
Lesser value from Design Table | 1 | 62.1 | 2.58 | 2.17 | 0.00774 | 0.0020145 | 0.00030945 | 0.010064 | 0.0065045 | 0.0006 | 10.8408 | 6 | 4.517
Results for Development | 1.08 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.0003342 | #VALUE! | #VALUE! | 0.000648 | #VALUE! | 6.48 | #VALUE!
Higher value from Design Table | 10 | 66.6 | 2.58 | 2 | 0.0774 | 0.018567 | 0.0030945 | 0.099061 | 0.064025 | 0.006 | 10.6708 | 60 | 44.4618

## Design Table
Lawrence Design Data From 2003 Wastewater Master Plan
Developed Acres | Tc minutes | 10 Yr "i" in/hr | WWP Peaking Factor
1 | 62.1 | 2.58 | 2.17
10 | 66.6 | 2.58 | 2
25 | 70.4 | 2.58 | 1.93
50 | 74.7 | 2.58 | 1.88
75 | 78.1 | 2.16 | 1.85
100 | 80.9 | 2.16 | 1.83
250 | 93 | 1.89 | 1.76
500 | 106.6 | 1.69 | 1.71
750 | 117.1 | 1.69 | 1.68
1000 | 126 | 1.54 | 1.66
1250 | 133.7 | 1.54 | 1.64
1500 | 140.8 | 1.4 | 1.63
1750 | 147.3 | 1.4 | 1.62
2000 | 153.3 | 1.3 | 1.61
2500 | 164.3 | 1.3 | 1.59
3000 | 174.2 | 1.21 | 1.58
4000 | 191.9 | 1.13 | 1.56
5000 | 207.5 | 1.13 | 1.54
7000 | 234.5 | 1 | 1.52
7500 | 240.6 | 0.9 | 1.51
10000 | 268.6 | 0.9 | 1.49
50000 | 526.4 | 0.53 | 1.37